## Slide 1: CE 3372 Water Systems Design
Lesson 12: OPEN CHANNEL FLOW (gradually varied FLOW)

## Slide 2: Flow in Open Conduits
Gradually Varied Flow Hydraulics
  Principles
  Resistance Equations
  Specific Energy
  Subcritical, critical, supercritical and normal flow.

## Slide 3: Description of Flow
Open channels are conduits whose upper boundary of flow is the liquid surface.
Storm sewers and sanitary sewers are typically designed to operate as open channels.
The relevant hydraulic principles are the concept of friction, gravitational, and pressure forces.

## Slide 4: Description of Flow
For a given discharge, Q, the flow at any section can be described by the flow depth, cross section area, elevation, and mean section velocity.
The flow-depth relationship is non-unique, and knowledge of the flow type is relevant.

## Slide 5: Open Channel Nomenclature
Flow depth is the depth of flow at a station (section) measured from the channel bottom.
y

## Slide 6: Open Channel Nomenclature
Elevation of the channel bottom is the elevation at a station (section) measured from a reference datum (typically MSL).
y
Datum
z

## Slide 7: Open Channel Nomenclature
Slope of the channel bottom is called the topographic slope (or channel slope).
y
Datum
So
1
z

## Slide 8: Open Channel Nomenclature
Slope of the water surface is the slope of the HGL, or slope of WSE (water surface elevation).
y
Datum
So
1
z
1
Swse
HGL

## Slide 9: Open Channel Nomenclature
Slope of the energy grade line (EGL) is called the energy or friction slope.
y
Datum
So
1
z
1
Swse
HGL
EGL
1
Sf
V2/2g
Q=VA

## Slide 10: Open Channel Nomenclature
Like closed conduits, the various terms are part of mass, momentum, and energy balances.
Unlike closed conduits, geometry is flow dependent, and the pressure term is replaced with flow depth.

## Slide 11: Open Channel Nomenclature
Open channel pressure head: y
Open channel velocity head: V2/2g
    (or Q2/2gA2)
Open channel elevation head: z
Open channel total head: h=y+z+V2/2g
Channel slope: So = (z1-z2)/L
  Typically positive in the down-gradient direction.
Friction slope: Sf = (h1-h2)/L

## Slide 12: Uniform Flow
Uniform flow (normal flow; pg 104) is flow in a channel where the depth does not vary along the channel.
In uniform flow the slope of the water surface would be expected to be the same as the slope of the bottom surface.

## Slide 13: Uniform Flow
Uniform flow would occur when the two flow depths y1 and y2 are equal.
In that situation:
  the velocity terms would also be equal.
  the friction slope would be the same as the bottom slope.
Sketch of gradually varied flow.

## Slide 14: Gradually Varied Flow
Gradually varied flow means that the change in flow depth moving upstream or downstream is gradual (i.e. NOT A WATERFALL!).
  The water surface is the hydraulic grade line (HGL).
  The energy surface is the energy grade line (EGL).

## Slide 15: Gradually Varied Flow
Energy equation has two components, a specific energy and the elevation energy.
Sketch of gradually varied flow.

## Slide 16: Gradually Varied Flow
Energy equation has two components, a specific energy and the elevation energy.
Sketch of gradually varied flow.

## Slide 17: Gradually Varied Flow
Energy equation is used to relate flow, geometry and water surface elevation (in GVF)
The left hand side incorporating channel slope relates to the right hand side incorporating friction slope.

## Slide 18: Gradually Varied Flow
Rearrange a bit
In the limit as the spatial dimension vanishes the result is.

## Slide 19: Gradually Varied Flow
Energy Gradient:
Depth-Area-Energy
  (From pp 119-123; considerable algebra is hidden )

## Slide 20: Gradually Varied Flow
Make the substitution:
Rearrange
Variation of
Water Surface Elevation
Discharge and
Section Geometry
Discharge and
Section Geometry

## Slide 21: Gradually Varied Flow
Basic equation of gradually varied flow
  It relates slope of the hydraulic grade line to slope of the energy grade line and slope of the bottom grade line.
  This equation is integrated to find shape of water surface (and hence how full a sewer will become)

## Slide 22: Gradually Varied Flow
Before getting to water surface profiles, critical flow/depth needs to be defined
  Specific energy:
    Function of depth.
    Function of discharge.
    Has a minimum at yc.
Energy
Depth

## Slide 23: Critical Flow
Has a minimum at yc.
Necessary and sufficient condition
for a minimum (gradient must vanish)
Variation of energy with respect to depth;
Discharge “form”
Depth-Area-Topwidth
relationship

## Slide 24: Critical Flow
Has a minimum at yc.
Right hand term is a squared Froude number. Critical flow occurs when Froude number is unity.
Froude number is the ratio of inertial (momentum) to gravitational forces
At critical depth the gradient is equal to zero, therefore:
Variation of energy with respect to depth;
Discharge “form”, incorporating topwidth.
Fr^2 =

## Slide 25: Depth-Area
The topwidth and area are depth dependent and geometry dependent functions:

## Slide 26: Super/Sub Critical Flow
Supercritical flow when KE > KEc.
Subcritical flow when KE<KEc.
  Flow regime affects slope of energy gradient, which determines how one integrates to find HGL.

## Slide 27: Finding Critical Depths
Depth-Area Function:
Depth-Topwidth Function:

## Slide 28: Finding Critical Depths
Substitute functions
Solve for critical depth
Compare to Eq. 3.104, pg 123)

## Slide 29: Finding Critical Depths
Depth-Area Function:
Depth-Topwidth Function:

## Slide 30: Finding Critical Depths
Substitute functions
Solve for critical depth,
By trial-and-error is adequate.
Can use HEC-22 design charts.

## Slide 31: Finding Critical Depths
By trial-and-error:
Guess this values
Adjust from Fr

## Slide 32: Finding Critical Depths
The most common sewer geometry
(see pp 236-238 for similar development)
Depth-Topwidth:
Depth-Area:
Remarks:
Some references use radius and not diameter.
If using radius, the half-angle formulas change.
DON’T mix formulations.
These formulas are easy to derive, be able to do so!

## Slide 33: Finding Critical Depths
The most common sewer geometry
(see pp 236-238 for similar development)
Depth-Topwidth:
Depth-Area:
Depth-Froude Number:

## Slide 34: Gradually Varied Flow
Energy equation has two components, a specific energy and the elevation energy.
Sketch of gradually varied flow.

## Slide 35: Gradually Varied Flow
Equation relating slope of water surface, channel slope, and energy slope:
Variation of
Water Surface Elevation
Discharge and
Section Geometry
Discharge and
Section Geometry

## Slide 36: Gradually Varied Flow
Procedure to find water surface profile is to integrate the depth taper with distance:

## Slide 37: Channel Slopes and Profiles
SLOPE | DEPTH RELATIONSHIP
Steep | yn < yc
Critical | yn = yc
Mild | yn > yc
Horizontal | S0 = 0
Adverse | S0 < 0
PROFILE TYPE | DEPTH RELATIONSHIP
Type-1 | y > yc AND y > yn
Type -2 | yc < y < yn OR yn < y < yn
Type -3 | y < yc AND y < yn

## Slide 38: Flow Profiles
All flows approach normal depth
  M1 profile.
    Downstream control
    Backwater curve
    Flow approaching a “pool”
    Integrate upstream

## Slide 39: Flow Profiles
All flows approach normal depth
  M2 profile.
    Downstream control
    Backwater curve
    Flow accelerating over a change in slope
    Integrate upstream

## Slide 40: Flow Profiles
All flows approach normal depth
  M3 profile.
    Upstream control
    Backwater curve
    Decelerating from under a sluice gate.
    Integrate downstream

## Slide 41: Flow Profiles
All flows approach normal depth
  S1 profile.
    Downstream control
    Backwater curve
    Integrate upstream

## Slide 42: Flow Profiles
All flows approach normal depth
  S2 profile.

## Slide 43: Flow Profiles
All flows approach normal depth
  S3 profile.
    Upstream control
    Frontwater curve
    Integrate downstream

## Slide 44: Flow Profiles
Numerous other examples, see any hydraulics text (Henderson is good choice).
Flow profiles identify control points to start integration as well as direction to integrate.

## Slide 45: WSP Using Energy Equation
Variable Step Method
  Choose y values, solve for space step between depths.
    Non-uniform space steps.
    Prisimatic channels only.

## Slide 46: WSP Algorithm

## Slide 47: Example

## Slide 48: Example
Energy/depth function
Friction slope function

## Slide 49: Example
Start at known section
Compute space step (upstream)
Enter into table and move upstream and repeat

## Slide 50: Example
Start at known section
Compute space step (upstream)

## Slide 51: Example
Continue to build the table

## Slide 52: Example
Use tabular values and known bottom elevation to construct WSP.

## Slide 53: WSP Fixed Step Method
Fixed step method rearranges the energy equation differently:
Right hand side and left hand side have the unknown “y” at section 2.
  Implicit, non-linear difference equation.
  Use SWMM or HEC-RAS for this (or take Open Channel Flow class)

## Slide 54: Gradually Varied Flow
Apply WSP computation to a circular conduit
Sketch of gradually varied flow.

## Slide 55: Depth-Area Relationship
The most common sewer geometry
(see pp 236-238 for similar development)
Depth-Topwidth:
Depth-Area:
Depth-Froude Number:

## Slide 56: Variable Step Method
Compute WSE in circular pipeline on 0.001 slope.
Manning’s n=0.02
Q = 11 cms
D = 10 meters
Downstream control depth is 8 meters.

## Slide 57: Variable Step Method
Use spreadsheet, start at downstream control.

## Slide 58: Variable Step Method
Compute Delta X, and move upstream to obtain station positions.

## Slide 59: Variable Step Method
Use Station location, Bottom elevation and WSE to plot water surface profile.
Chart: Station Distance (meters)
| 0.0 | -200.429601920282 | -400.8792270251688 | -601.3523838695434 | -801.8529991882101 | -1002.385528789935 | -1202.955088775125 | -1403.567614653376 | -1604.230057835206 | -1804.950631806243 | -2005.739124374496 | -2206.60729821857 | -2407.569410341131 | -2608.642893162908 | -2809.849257776632 | -3011.215306330056
Bottom | 0 | 0.20043 | 0.40088 | 0.60135 | 0.80185 | 1.0024 | 1.203 | 1.4036 | 1.6042 | 1.805 | 2.0057 | 2.2066 | 2.4076 | 2.6086 | 2.8098 | 3.0112
WSE | 8 | 8.0004 | 8.0009 | 8.0014 | 8.0019 | 8.0024 | 8.003 | 8.0036 | 8.0042 | 8.005 | 8.0057 | 8.0066 | 8.0076 | 8.0086 | 8.0098 | 8.0112
Flow

## Slide 60: Next Time
Introduction to SWMM